## Slide 1
Design and Development of a Cost Optimized Timing System for Steady State Superconducting Tokamak (SST-1)
J. DHONGDE, A. Kumar, D. Raju & SST-1 Operations Division
Institute for Plasma Research,
Gandhinagar
India
The 12th IAEA Technical Meeting on Control, Data Acquisition and Remote Participation for Fusion Research (CODAC 2019), Daejeon, Republic of Korea
13 May 2019
Acknowledgements
Praveena Kumari & Rachana Rajpal, Front End Electronics Division (Resources for prototype development)
Kirit Vasava & Drafting section ( For design of 1U Rack mountable enclosures)
Vijaykumar Patel & Workshop division ( For fabrication of 1U Rack mountable enclosures)
Hitesh Chudasma, Atish Sharma, Kirti Mahajan & Data Acqusition – Control Division (For testing and validation)
Institute for Plasma Research
ID - 443

## Slide 2
SST-1 sub systems
Spatially distributed & Heterogeneous Platform systems
RCC Power
Supply
Central
Control
Room
DAQ
Systems-2
DAQ
Systems-1
ICRH
Ohmic
Power
Supply
LHCD
ECRH
Plasma
Control
System
SST-1
TF Power
Supply
Cryogenics
Vacuum
Magnet
~ 256 m
#Not actual scale (for visualization only)

## Slide 3
SST-1 sub systems – with Timing System interface
RCC Power
Supply
Central
Control
Room
DAQ
Systems-2
DAQ
Systems-1
ICRH
Ohmic
Power
Supply
LHCD
ECRH
Plasma
Control
System
SST-1
TF Power
Supply
Cryogenics
Magnet
Vacuum
~ 256 m
t= -50ms
t= 150ms
t= -2441ms
t= 50ms
t= 0ms
t= 0ms
t= 0ms
t= 0ms
t= -500ms
Clock =
10kHz,
100kHz
1MHz, 10MHz
Clock =
10kHz,
100kHz
1MHz, 10MHz
All trigger timings are configurable for all Timing system modules

## Slide 4
SST-1 old Timing System
Based on VME Platform ( ~ 15Years). Custom VME Timing System cards were in house designed and developed.
Master – Slave configuration connected in star configuration. Optical Network – Multimode, 62.5/125 µm.
Provide fast timing signals (clock & triggers) to various sub systems during plasma discharges
Master VME Node (Central Control Room)
  - Broadcast experiment sequence @ minimum resolution of 1µs
  - Provide 20MHz Stable OCXO based clock to slave
  Record events with 32bit time stamp
Slave VME Node (ECRH, Power Supply etc.)
  - Recover & regenerate different clocks (10MHz,1MHz etc.) from 20MHz clock
  - Generate different channel outputs
  - Provide optically isolated channel inputs
Timing System card inventory got exhausted
Sub system hardware advancement also started ( Systems migrated from VME to PXI, PXIe etc.)
Power
Supply
Central
Control
Room
DAQ
Systems-2
DAQ
Systems-1
ICRH
Ohmic
Power
Supply
LHCD
ECRH
SST
Reference:(1)

## Slide 5
Power
Supply
Central
Control
Room
DAQ
Systems-2
DAQ
Systems-1
ICRH
Ohmic
Power
Supply
LHCD
ECRH
SST
New Timing System Requirement
2. Timing System which supports existing optical fiber network and star topology
3. Timing System – provide single interface to heterogeneous platform systems
1. Timing System with performance
parameters comparable
to old system
4. Easy integration
with sub system i.e. minimal modification on hardware as well as on software part at sub system end
VME >> PXIe

## Slide 6
SST-1 Timing System
Power
Supply
Central
Control
Room
DAQ
Systems-2
DAQ
Systems-1
ICRH
Ohmic
Power
Supply
LHCD
ECRH
SST
DAQ Systems
Plasma Control System
Power Supply
ECRH
LHCD
Ohmic Power Supply
ICRH
Central Module
Sub system
module
Simplified block diagram- Timing System modules with fiber optic network
Central module(Master ), Sub system module (Slave )

## Slide 7
SST-1 New Timing System
Central Module
Plasma Control System
Power Supply
ECRH
LHCD
Ohmic Power Supply
ICRH
Sub system
module
DAQ Systems
A platform independent
Standalone, 1U Rack mountable modules
  Central module (Master)
  Sub system module (Slave)
Master – Slave configuration connected in star configuration. Optical Network – Multimode, 62.5/125 µm
Provide real time event ( trigger) distribution to various sub systems during plasma discharges #
Modules designed using Xilinx’s Artix-7 FPGA
# Version -1 development boards

## Slide 8
Few Specifications | Old Timing System | New Timing System
Synchronous, Shutdown sequence generation resolution | 1 µs | 10 µs
Time Stamp resolution of events | 50 ns | 1 µs
Event latency | 3.8 µs (100m optical fiber) | 4µs ( 3m optical fiber)
Real time, Deterministic | Yes | Yes
No. of sub systems that can be connected | 16 | 8
Sub system Asynchronous inputs | 16 | 8
Sub system channel outputs ( as triggers) | 4 (expandable) | 8
Total number of events (reserve events, sync, shut down events …) | 65535 | 255
Trigger output, Asynchronous input signal interface | TTL | TTL
Synchronous Clock distribution | 1kHz/10kHz/100kHz/1MHz/10MHz | Not in present version#
GPS – IRIG B Interface | Yes | Not in present version#
SST-1 New Timing System v/s Old
# Version -1 does not include clock synchronization

## Slide 9
Timing System - Central & Sub system modules
Xilinx
Artix-7
FPGA
Optical Transmitter
HFBR-1414Z
Optical Receiver
AFBR-2418Z
Xilinx
Artix-7
FPGA
Xilinx
Artix-7
FPGA
Optical Transmitter
HFBR-1414Z
Optical Receiver
AFBR-2418Z
Optical Transmitter
HFBR-1414Z
Optical Receiver
AFBR-2418Z
Optical Transmitter
HFBR-1414Z
Optical Receiver
AFBR-2418Z
10-bit Serial
Asynchronous
6.25Mbps
62.5/125 µm multimode fiber
50MBd
TTL Compatible
Central module
Sub system module -1
Sub system module -8
Reference:(2,3,4)

## Slide 10
Complete Sub System module
OrangePi (open-source single-board computer) runs Linux
Orange Pi provides Ethernet interface (10/100Mbps) to sub system and central module ( for non real time data communication)
OrangePi to FPGA communication – UART 9600bps
Timing System configurations for either sub system module or central module are communicated to FPGA through OrangePi
Optical Transmitter and receiver test with 10MHz signal
10 bit data Transmit at 6.25Mbps (8 bit data, 1 start, 1 stop)
Input Output Interface
Transmit FIFO
Receive FIFO
Transmit Section
Receive Section
UART
Timing Logic
BAUD generator
100MHz
RAM
Artix-7 FPGA
Orange Pi
Board
Optical Transmitter
HFBR-1414Z
Optical Receiver
AFBR-2418Z
Buffer (Output)
Opto – Coupler ( Input)
Configuration logic
Ethernet
10/100Mbps
Note : Central module – additional Multiple Transmitter and receiver sections are present.
Reference:(5,6,7,8)

## Slide 11
Transmit FIFO
Receive FIFO
Transmit Section
Receive Section
UART
Timing Logic
BAUD generator
100MHz
RAM
Artix-7 FPGA
Orange Pi
Board
Optical Transmitter
HFBR-1414Z
Optical Receiver
AFBR-2418Z
Buffer (Output)
Opto – Coupler ( Input)
Input Output Interface
Ethernet
10/100Mbps
Configuration logic
1. No use of dedicated discrete hardware resources for memory
E.g. RAM, DPRAM
2. No use of dedicated discrete hardware resources for optical data transmission interface
E.g. Serializer , Deserializer
3.
No specific platform based development
E.g. VME
New Timing System – What’s difference ?

## Slide 12
Central & Sub system modules
Central Module board
1U Rack mountable central module
Sub system Module ( slave ) board
1U Rack mountable sub system module
  Maximum Slave modules that can be connected = 8
  Synchronous & Shut down sequence event generation time
  resolution = 10 μS
  Event time stamp resolution = 1μs
  Maximum number of synchronous & shut down
  sequence events = 255
  Maximum event time stamp duration = 4294.96s (~ 71.58 min)
  TTL Channel Outputs = 8 ( Low to High )
  TTL Channel Inputs = 8 ( Rising edge i.e. low to high logic)
  Minimum pulse width for channel outputs = 1µS
  Maximum pulse width for channel output = 429.49 sec
  Minimum pulse width at channel input = 500ns (as event)
  Channel outputs for multiple events or same event

## Slide 13
Timing System Client application
Timing System Client
Linux based application
Client-Server architecture
Connects & Configures all Timing System modules
Issues commands to generate experiment sequences
Online event information to operator
Channel Pulse Definition
Configures experiment sequence
Configures sub system modules for trigger pulse outputs
Event log

## Slide 14
Timing System - Performance, Results & Validation
Set Up - Central Module ( Master) – and Two Sub system modules (Slave)
Central Module
Power Supply
ECRH
LHCD
Ohmic Power Supply
ICRH
Sub system -1
module
DAQ Systems
Sub system -2
module
OSCILLOSCOPE (4 Analog, 16 DIGITAL CH)
Input
Input
DI0 – DI7
DI0 – DI7
DO0 – DO7
DO0 – DO7
Output
Output

## Slide 15
Output
Pulse
missed
Sub system 1
Output
Pulses
missed
Sub system 2
Output
Pulses
appeared
Sampling data bits (@ Receiver -16 x Bit rate)
But, only single sampling point to decode received data bit
Multiple sampling points with averaging – to decode received data bit
Trigger
Performance, Results & Validation
Reference:(9)

## Slide 16
Performance, Results & Validation
Central Module (Master) – Experiment events (Synchronous) sequence at resolution of 10 µs
Pulse outputs corresponding to Synchronous Events on Two sub systems
D0-D7 : Sub system1 outputs
D8-D15 : Sub system 2 outputs
Event Log file

## Slide 17
Performance, Results & Validation
Central Module (Master) – Experiment events (Synchronous) sequence test
Synchronous events at slaves- Generate pulse outputs on receiving synchronous events (7x8) and shutdown events (7x8) on all eight outputs of two different slave modules
D0-D7 : Sub system1 outputs
D8-D15 : Sub system 2 outputs

## Slide 18
Performance, Results & Validation
Central Module ( Master) board – Event log resolution of 1µs
Event time stamp at Master – Two asynchronous events generated simultaneously by two slaves
(* Note – Sub system1 – Async event 0xf7
Sub system 2 – Async event 0xee)
Event time stamp at Master – 16 asynchronous events generated simultaneously by two slaves
(* Note –
Sub system1 – Async events from 0xf7 to 0xfe
Sub system2 - Async events from 0xee to 0xf5)

## Slide 19
Performance, Results & Validation
Sub system Module – Event Latency Test on two different sub system modules (3m optical fiber)
1000 Pulses at 1 sec interval on any one of input of slave module 1, which then generates an event to Master module. Generate a channel pulse output for this event on other slave module 2.
Ch1: Pulse input also observed on oscilloscope ( as an input to sub system module 1)
Ch2: Output generated on sub system module 2 by the corresponding event generated due to above pulse input
#Note- Voltage level of Ch1 on oscilloscope is less, as it is measured across opto-coupler input.

## Slide 20
Performance, Results & Validation
Sub system Module – Simultaneous Asynchronous events (3m optical fiber)
Asynchronous events - Generate asynchronous events by simultaneously applying 7 consecutive pulses on all eight inputs of two different slave modules. Configure pulse outputs for the generated asynchronous events.
D0-D7 : Sub system1outputs
D8-D15 : Sub system 2 outputs

## Slide 21
Field Testing – Similar to actual plasma shot scenario
Generate experiment sequence similar to actual scenario
Log file – registers all events with time stamp
Real time event sequence generation (ECRH Launch trigger in reference to actual plasma shot scenario)

## Slide 22
New Timing System Cost (Estimations)
#Version1 - Module Costs* (Indian Rupees Rs)(U.S $)
* Excludes the cost of material available with Institute for Plasma Research Stores department, Workshop, Job hours etc.
Central module ( Per unit) | Rs. 41,698 /- approx. (600$)
Sub system module ( Per unit ) | Rs. 25,168 /- approx. (360$)
Timing System with 1 Central module and 8 sub system modules | Rs. 2,43,042/- approx. (3475$)
# Version 1 ( Without Clock Synchronization & GPS IRIGB interface)

## Slide 23
Further Development - Clock Synchronization ( In Progress)
Central Module
Power Supply
ECRH
LHCD
Ohmic Power Supply
ICRH
Sub system -1
module
DAQ Systems
Input
DI0 – DI7
DO0 – DO7
Output
Sub system
Clock
Clock Outputs
(10MHz / 1MHz / 100kHz/10kHz/
1kHz)
Clock
Outputs
Clock
Trigger
Clocks and their calculated Cumulative Time Errors (CTE)
Clock source under test | Frequency (MHz) | Stability (ppm) | CTE over 10 second | CTE over 60 second | CTE for 3600 second
Local Artix-7 oscillator SiT8008 | 100MHz | 20 ppm | 200 µs | 1.2 ms | 72 ms
OCXO-2050 (Old Timing System) | 20 MHz | 0.1ppm | 1 µs | 6 µs | 360 µs
Proposed | 20 MHz | 0.02 ppm | 0.2 µs | 1.2 µs | 12 µs
Reference:(10)

## Slide 24
Further Development - GPS IRIG-B Interface, Event prioritization, Error handling ( In progress)
Propagation delay compensation
Event prioritizing logic at Central sub system module
Error handling features ( Parity, CRC …)
Develop GPS IRIG-B interface for the modules. (For GPS synchronization and GPS time)

## Slide 25
Summary
A Platform independent, stand alone, 1U rack mountable timing system is designed, developed and tested.
The performance test results are comparable and acceptable.
The development cost is observed to be optimized considering the simple design adopted.
Design can be implemented with other FPGAs ( different make).
New in-house design will be advantageous and it can be easily adapted for time synchronization applications in small, medium size tokamaks or experimental devices irrespective of hardware/ software platforms.

## Slide 26
References
Overview of time synchronization system of steady state superconducting tokamak SST-1 , 1A. Kumar, H. Masand, J. Dhongde et. al, Fusion Engineering and Design 112 (2016) 683–686
https://www.xilinx.com/products/silicon-devices/fpga.html
HFBR-14xxZ and HFBR-24xxZ Series (Broadcomm), Low-Cost, 820 nm Miniature Link Fiber Optic Components with ST®, SMA, SC and FC Ports - Data sheet
AFBR-24x8xZ(Avago Technologies) DC-50MBd Miniature Link Fiber Optic Receiver-Data sheet
Ultra-Compact UART Macros for Spartan-6, Virtex-6 and 7-Series, Ken Chapman, 29th March 2013
The Design of High Speed UART, J. Norhuzaimin and H.H Maimun, 2005 Asia Pacific Conference on Applied Electomagnetics Proceedings, December 20-21, 2005
FPGA Module with Xilinx Artix-7 XC7A35T (TE0725-03-35-2C), Trenz Electonic (https://shop.trenz-electronic.de/en/TE0725-03-35-2C-FPGA-Module-with-Xilinx-Artix-7-XC7A35T-2CSG324C-2x50-pin-header-3.5-x-7.3-cm)
http://www.orangepi.org/orangepizero/
UART Receiver Synchronization: Investigating the Maximum Tolerable Clock Frequency Deviation, Indian Journal of Science and Technology, Vol 10(25), July 2017
The AD9548 as a GPS Disciplined Stratum 2 Clock, Ken Gentile ( Analog Devices – AN 1002 Application Note)

## Slide 27
Thank You