## Slide 1
DESIGN OF SECONDARY SODIUM SYSTEM BASED DECAY HEAT REMOVAL SYSTEM FOR FUTURE FAST BREEDER REACTOR
Paper ID: 502
Pritam Kumar Patel
Reactor Design and Technology Group (RDTG),
Indira Gandhi Centre for Atomic Research (IGCAR),
India

## Slide 2
Outline of Presentation
1/17
Brief description of Fast Breeder Reactor (FBR) 1&2
Decay Heat Removal Systems (DHRS) - Background
Requirement of SSDHRS
Literature survey
Required heat removal capacity of SSDHRS
Conceptual design of SSDHRS
Process design of SSDHRS: Forced flow
Optimization studies of AHX
Parametric studies
Sodium pump selection and need of bypass line to SSDHRS
Design finalisation
Method for calculation of Heat capacity under natural circulation
Results with only natural circulation
Conclusion

## Slide 3
2/17
Brief description of FBR 1&2
Schematic of FBR 1&2
FBR 1&2 is a twin reactors
Power capacity/unit: 1500 MWt
: 600 Mwe
Fuel: Mixed Oxide (MOX)
Coolant : Sodium
Type : Pool
Secondary loop/unit : 2 No’s
Major equipment in Secondary loop: 2 IHX

## Slide 4
3/17
Decay Heat Removal Systems (DHRS)
Decay heat removal systems for FBR 1&2
Background:
Decay Heat Removal (DHR) system removes the heat generated in the core after reactor shutdown.
In PFBR, there are two diverse paths for DHR:
Operation Grade Decay Heat Removal Circuit(OGDHR)
Saftey Grade Decay Heat Removal Circuit (SGDHR)
For FBR 1&2 it is planned to have an additional DHR: called Safety Grade Decay Heat Removal System (SSDHRS)
SSDHRS:
SSDHRS loops are integrated to Secondary Sodium Main Circuit (SSMC) .

## Slide 5
4/17
Requirement of SSDHRS
Need of an additional decay heat removal system:
To reduce the number of demands on SGDHRS.
Mainly to cater to the planned activity viz. fuel handling and other maintenance conditions, if OGDHR system is not available.
SSDHRS is seismically qualified (unlike OGDHR), Hence the reliability of the SSDHR system improves the reliability of the overall DHR system significantly.
Features of SSDHRS system:
Designed to operate on active mode.
Provided with class III power.
It is capable to work in passive mode with reduced capacity.

## Slide 6
Literature survey-SSDHRS
BN 800 (RUSSIA) :
BN800 is a pool type reactor with 800 MWe and 2100 MWt.
It has three secondary loops and each having one DHRS.
DHRS on secondary system has 2 AHX and 2 EMP per loop.
In case of failure of EMP, the loop can also operate using SSP.
5/17
  MONJU (JAPAN).
It is a loop type reactor with 280 MWe and 714MWt.
It has three secondary loops and each having one DHRS.
DHRS on secondary system has 1 AHX and 1 EMP per loop.
No provision is provided to operate on SSP.
Contd. (1/2)

## Slide 7
Literature survey-SSDHRS
6/17
SUPERPHENIX (FRANCE):
It is a pool type reactor with 1250 MWe and 3000 MWt.
It has four secondary loops and each having one DHRS
DHRS on secondary system has 1 AHX per loop with no EMP.
It operates only on SSP using a separate auxiliary motor.
All the reactors are deigned to operate on active mode.
Also provision is made for passive mode with reduced capacity.
(2/2)

## Slide 8
7/17
Required heat removal capacity of SSDHRS
PFBR’s SGDHRS: 24 MWt, with 3 out of 4 circuits available (i.e., n-1 criteria)
(DHR capacity = 1.92 % of the total power of 1250 MWt).
FBR 1&2 SSDHRS: DHR capacity = 1.92 % of the total power of 1500 MWt
= 28.8 MWt (approx. to 30 MWt)
Considering
The space constraints
Optimization of the overall cost
2 secondary sodium main loops in FBR 1&2
SSDHR in each secondary sodium loop is designed for 15MWt.

## Slide 9
Conceptual design of SSDHRS
8/17
Schematic of SSDHRS for forced flow:
PSP : Primary Na Pump
IHX : Intermediate Heat Exchanger
ST : Surge Tank
SG : Steam Generator
SSP : Secondary Na Pump
AHX : Air Heat Exchanger
Contd. (1/2)

## Slide 10
Conceptual design of SSDHRS
9/17
AIR BLOWER:
Blower for active operation mode.
To increase reliability, blower is provided with class 3 power.
Air Heat Exchanger:
Type: Cross flow type shell and tube Heat eXchanger (HX)
LOCATION OF AHX:
It is planned to place inside SGB, below surge tank which allows gravity flow.
Hence, there is no need of additional tank for expansion of sodium.
3D layout of SSDHRS
ST
AHX
SSP
From IHX
To IHX
The sectional view of the AHX
(2/2)

## Slide 11
Process design of SSDHRS: Forced flow
10/17
IHX
(2 no's)
ST
AHX
(1 no's)
Decay heat
Hot pool
TPi=544 C
Assume (3) : PSP operates on 20 % flow during decay heat removal
TPo= 531.5 C
Assume (1):
4 % SSP full flow
Q=ms Cs (TSo - TSi)
Q= (UA θLMTD)IHX
TSi=454.3 C
TSo=544 C
TAi=40 C
Assume (2): TAo=286.5 C
52.8 m3/sec
Q= ma Cp (TAo-TAi)
Q= (UA θLMTD) AHX
No of tube= 129
Q= ma Cp (TPi - TPo)
3 SGs
SSP
BLOWER
ON
PSP-ON
Heat Removal capacity : 15 MW
Aim:
Design of blower
Design of AHX
Select an operating point for SSP

## Slide 12
11/17
Optimization studies of AHX
Parametric study of sodium flow rate on AHX design for an air flow rate of 52.8 m3/sec
Parametric study of air flow rate on AHX design for an sodium flow rate of 4% nominal SSP flow
Velocity inside AHX tube
No of tube in AHX
Velocity in AHX shell side
No of tube in AHX
Velocity limited to 2 m/s
Assume (1): 4 % SSP full flow
Assume (2): air flow rate of 52.8 m3/sec

## Slide 13
Parametric studies
12/17
Heat removal capacity of SSDHR at various primary sodium temperatures
Performance of SSDHRS at various primary sodium flow rates
Assume (3) : PSP operates on 20 % flow during decay heat removal
% Flow of primary sodium pump

## Slide 14
Pump selection and need of bypass line to SSDHRS
13/17
PUMP SELECTION:
Flow requirement of SSDHRS for FBR 1&2 is 568.6 m3/h (4 % of nominal), (Existing EM pump is not adequate).
SSP will be operated with reduced flow.
REQUIREMENT OF BYPASS LINE TO SSDHRS:
Head generated by the SSP for 4 % flow is not adequate for SSDHRS circuit.
Bypass line is provided in the circuit to increase flow so that, SSP can be operated in best efficiency zone.
Bypass line is designed to have SSP flow of 22 % of nominal capacity. Total flow through SSP is 26 %.
Typical pump - system characteristic curves for SSDHRS and SSMC
Bypass loop
Bypass line to SSDHRS
SSDHRS Circuit
SSP
ON

## Slide 15
14/17
Finalized design
Process flow sheet of secondary sodium decay heat removal circuit

## Slide 16
Method for calculation of Heat capacity under natural circulation
15/17
IHX
(2 no's)
SSP-OFF
PSP-ON
ST
AHX
(1 no's)
Decay heat
Blower-OFF
TPi=544 C
20 % of full flow
TPo
By pass line
TSi
TSo
TAi= 40 C
TAo
Air flow rate
Known variable: IHX and AHX geometry, TPi, Tai, Assumption: Primary side flow is 20 % of full flow
Secondary flow rate
Eq 1. ms Cs (TSo - TSi)= ma Cp(TPi - TPo)
Eq 2. ms Cs (TSo - TSi)= (UA θLMTD)IHX
Eq 3. ms Cs(TSo - TSi)= ma Cp (TAo - TAi)
Eq 4. ms Cs(TSo - TSi)= (UA θLMTD)AHX
Eq 5. (ρcold - ρhot ) g Hs = (DP on secondary side)
Eq 6. (ρcold - ρhot ) g Ha = (DP on air side)
= 544 C
= 449.5 C
= 536.8 C
= 339.8 C
= 73 kg/sec
= 25 kg/sec
6 unknown variable: TPo, TSi, TSo, TAo, Secondary flow rate (ms), Air flow rate (ma)
Derived quantity: Heat transfer capacity (Q)
IHX details
AHX details
Q= ms Cs (TSo - TSi)= ma Cp(TPi - TPo) = ma Cp (TAo - TAi) =8.6 MW
Chimney

## Slide 17
Results with only natural circulation
16/17
Evolution of secondary Sodium and air flow rate during natural conv.
Effect of chimney height on heat removal capacity by natural circulation
Heat removal capacity between forced and natural convection

## Slide 18
Conclusion
The no of design basis events for which SGDHR is called has been brought down.
Process design of SSDHRS is carried out for active mode (15 MWt) per loop.
Process path, piping layout and component locations are finalized considering existing FBR 1&2 (2×600 MWe) layout.
SSP shall be operated at 26 % nominal flow with 22 % of nominal flow bypassed.
Primary sodium flow required for active operation is less than 3 % nominal achieved by natural circulation.
For chimney of 30 m height, SSDHRS with passive mode can remove 8.6 MWt per loop.
17/17

## Slide 19
THANK YOU