Modelling and Simulation of Source Term for Sodium-Cooled Fast Reactor under Hypothetical Severe Accident: Primary System/Containment System Interface Source Term Estimation

Y. ONODA

Japan Atomic Energy Agency (JAEA)

O-arai, Japan

Email: onoda.yuichi@jaea.go.jp

JOHN ARUL A.

Indira Gandhi Centre for Atomic Research (IGCAR)

Kalpakkam, India

I. KLIMONOV

Nuclear Safety Institute of the Russian Academy of Sciences (IBRAE RAN)

Moscow, Russian Federation

S. DANTING

North China Electric Power University (NCEPU)

Beijing, China

Email contact of corresponding author: onoda.yuichi@jaea.go.jp

Abstract

Three Work Packages (WPs) were defined in this Coordinated Research Project (CRP) whose objective was to estimate fission-product-transportation behavior inside the reference pool-type sodium-cooled fast reactor (SFR) volumes (i.e., in-primary vessel, cover gas system and in-containment building) at different time scales under severe accident conditions. This WP, WP-2, is dedicated to estimate the primary system/containment system interface source term using improved models and tools to evaluate sodium ejection via leak paths through the top shield of the reactor vessel. The mass of primary sodium instantaneously ejected into the Reactor Containment Building (RCB) was evaluated as a common benchmark problem which will be the input for the subsequent WP, WP-3, where radionuclide chemical composition and distribution, and sodium combustion within the containment system will be evaluated. The exercises were carried out for a reference pool type SFR of 1250 MWth capacity with mixed oxide fuel. The accident sequence to be considered is Unprotected Loss of Flow Accident (ULOFA) which is assumed to result in a core damage with release of radionuclides into the primary coolant and cover gas. Four organizations, NCEPU (China), IBRAE RAN (Russian Federation), IGCAR (India) and JAEA (Japan) finally participated in this WP. Reference case calculation using a common pressure history and sensitivity study were carried out. The total amount of the ejected sodium onto the top shield for reference case was in a good agreement between the participants. The results of the sensitivity study revealed that the change of the parameters regarding uncertainty, such as inlet pressure, outlet pressure, cross-sectional area, and loss coefficient bring about the change of leaked mass in the range of several tens of %.

  - INTRODUCTION

Towards improving the current state of the art for modelling the in-vessel and in-containment source terms IAEA launched the Coordinated Research Project (CRP) in which participants from nine countries are doing benchmark simulations for the source term estimation with different models and tools. The technical aspects to be addressed are divided into three Work Packages (WPs). First is WP-1, the in-vessel source term estimation, consisting of risk important fission product distribution in the fuel pins, their release mechanisms into the coolant and subsequent reaction and transport in the coolant and release to the cover gas. Second is WP-2, the primary system/containment interface source term estimation consisting of models for the cover gas, sodium ejection and radionuclide chemical composition and distribution in the containment. The third part is WP-3, the estimation of the fission product evolution within the containment considering sodium burning scenarios, aerosol behavior and physical boundary conditions. The scope of the CRP was to predict and compare in-vessel, interface and in-containment radio nuclide release fractions using improved models and tools.

In order to benchmark the development of mechanistic models for the assessment of in vessel and in containment source term, a reference Sodium-cooled Fast Reactor (SFR) has been defined [1]. The reference reactor is a generic model loosely based on the Prototype Fast Breeder Reactor, currently under commissioning in India. The reference reactor is pool type SFR which consists of a primary sodium circuit, two secondary sodium circuits and a steam water circuit. Primary sodium circuit consists of core, control plug, hot pool, cold pool, two primary sodium pumps, four Intermediate Heat Exchangers (IHX), and Safety Grade Decay Heat Removal System (SGDHRS).

Four organizations, NCEPU (China), IBRAE RAN (Russian Federation), IGCAR (India) and JAEA (Japan) were finally participated in this work package, WP-2. NCEPU calculate the leakage of liquid sodium using CFD code, FLUENT. IBRAE RAN did the simulations with their own code EUCLID/V2. IGCAR used NETFLOW codes for simulations. JAEA used PLUG code for the calculations of sodium ejection.

This WP is dedicated to estimate the primary system/containment system interface source term using improved models and tools to evaluate sodium ejection via leak paths through the top shield of the reactor vessel. The mass of primary sodium instantaneously ejected into the Reactor Containment Building (RCB) was evaluated as a common benchmark problem which will be the input for the subsequent WP, WP-3, where radionuclide chemical composition and distribution, and sodium combustion within the containment system will be evaluated.

In the paper, the scope of this study, calculation methods of each institution, and calculation results and discussion are respectively described.

  - SCOPE OF THIS STUDY

Objective

The objective of this WP, WP-2, is to evaluate the mass of primary sodium instantaneously ejected into the RCB through the leak paths within the top shield. Reference case calculation is carried out by each participant using a common pressure history as a benchmark analysis. Participants also do the sensitivity study for the purpose to investigate the uncertainty along with their own interests.

Accident Sequences

The accident sequence to be considered is Unprotected Loss of Flow Accident (ULOFA). This event is assumed to result in a core damage event with release of radionuclides into the primary coolant and cover gas. ULOFA transient is initiated due to loss of primary coolant flow resulting from loss of power to both the primary pumps and failure to shut down the reactor. This leads to coolant temperature rise and voiding in the upper part of highly rated channel. As void spreads widely in core region large positive reactivity is introduced. It leads to power excursion and finally to rapid increase in clad and fuel temperatures which results in Core Disruptive Accident (CDA).

There are two accident progression sequences of ULOFA: energetic one and non-energetic one. Energetics is defined as the event which gives mechanical load on the reactor vessel as a result of core disassembly. In a core disassembly phase, fuel vapor is generated due to nuclear heating. Then CDA bubble, which is mixture of fuel, steel vapor and fission gas, and molten core material, expands into upper plenum via upper core structure. After that sodium vapor is generated due to Fuel-Coolant Interaction (FCI) in the upper plenum. If the mechanical energy generated is sufficiently large, sodium slug impacts on the lower surface of the top shield. The consequences of the slug impact can result in the following: one is the reactor vessel failure and the other is the sodium ejection via gaps between shield plugs which leads to sodium combustion within RCB. In this WP, we focused on investigating sodium ejection behaviour via gaps between shield plugs.

Analysis Condition

Schematic of top shield is shown in Fig. 1. The major leak paths in the top shield are the annular gaps between the Roof Slab (RS) and Large Rotating Plug (LRP), and LRP and Small Rotating Plug (SRP). The other penetrations in the RS are passage for IHX, Primary Sodium Pumps, DHX, Fuel Transfer Port, Hot Pool Level Detector (HPLD), Cold Pool Level Detector (CPLD), Delayed Neutron Detector (DND), Sodium Fill and Drain Lines, Argon Feed and Outlet Lines, Sodium Purification Lines and Fuel Transfer Machine Bottom Frange. The penetrating paths in the SRP are due to Control Plug, Oval Shield Plug of Transfer Arm and Guide Tube of Transfer Arm. Control plug has penetrating paths due to Control and Safety Rod Drive Mechanisms (CSRDM), Diverse Safety Rod Drive Mechanisms (DSRDM), Failed Fuel Location Modules (FFLM). All the components are large and are secured with adequate number of bolts (~150), with good redundancy. Rupture of pipe lines is not postulated as the lines are designed to bear the static equivalent of dynamic pressure under CDA. Hence, no ejection of the sodium from reactor vessel beyond top shield through the leak paths between components is considered.

Fig. 1.	Schematic of top shield.

The top shield is designed as described above, but in this WP, it is hypothesized that each of the above leak paths is opened with a certain gap in advance, that is, the fastening bolt is assumed to be statically stretched. Then, the amount of sodium ejected from the reactor vessel to the upper surface of the top shield through the leak path is evaluated. The name of the leak path is represented by a combination of shield plugs in contact with the leak path as shown in Table 1, where the name, type, number and flow path width of each leak path are shown. The leak paths to be evaluated are classified into seven types as shown in Table 1. Dimensions of sodium leak paths of type 5 is listed in Table 2.

TABLE 1.	CHARACTERISTICS OF THE LEAK PATH

| No. | Path name | Type | Qty | δ* |  | No. | Gap name | Type | Qty | δ* |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | RS-LRP | 1 | 1 | 5.0 |  | 9 | RS-FTP | 5 | 1 | 0.5 |
| 2 | LRP-SRP | 2 | 1 | 5.0 |  | 10 | RS-FTMBF | 5 | 1 | 0.5 |
| 3 | SRP-OSP | 3 | 1 | 1.0 |  | 11 | RS-DND | 5 | 1 | 0.5 |
| 4 | SRP-CP | 5 | 1 | 1.0 |  | 12 | OSP-GT | 4 | 1 | 1.0 |
| 5 | RS-IHX | 5 | 4 | 0.5 |  | 13 | CP-FFIM | 5 | 3 | 0.3 |
| 6 | RS-PSP | 5 | 2 | 0.5 |  | 14 | RS-HPLD | 5 | 1 | 0.5 |
| 7 | RS-CPLD | 5 | 1 | 0.5 |  | 15 | CP-CSRDM | 6 | 9 | 0.2 |
| 8 | RS-DHX | 5 | 4 | 0.5 |  | 16 | CP-DSRDM | 7 | 3 | 0.2 |

*δ: width of the leak path which dominates the leak rate (mm)

TABLE 2.	DIMENSIONS OF SODIUM LEAK PATHS OF TYPE 5

| No. | Path name | Type | Qty | ΦD1(m) | ΦD2(m) | L1(m) | L2(m) | δ1(m) | δ2(m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4 | SRP-CP | 5 | 1 | 2.25 | 2.29 | 1.8 | 0.05 | 0.02 | 0.001 |
| 5 | RS-IHX | 5 | 4 | 2.18 | 2.2 | 1.8 | 0.06 | 0.02 | 0.0005 |
| 6 | RS-PSP | 5 | 2 | 2.18 | 2.2 | 1.8 | 0.06 | 0.02 | 0.0005 |
| 7 | RS-CPLD | 5 | 1 | 0.68 | 0.7 | 1.8 | 0.15 | 0.01 | 0.0005 |
| 8 | RS-DHX | 5 | 4 | 0.56 | 0.58 | 1.8 | 0.06 | 0.01 | 0.0005 |
| 9 | RS-FTP | 5 | 1 | 0.56 | 0.58 | 1.8 | 0.14 | 0.01 | 0.0005 |
| 10 | RS-FTMBF | 5 | 1 | 0.56 | 0.58 | 1.8 | 0.14 | 0.01 | 0.0005 |
| 11 | RS-DND | 5 | 1 | 0.33 | 0.35 | 1.8 | 0.14 | 0.01 | 0.0005 |
| 13 | CP-FFIM | 5 | 3 | 0.31 | 0.316 | 2.310 | 0.052 | 0.003 | 0.0003 |
| 14 | RS-HPLD | 5 | 1 | 0.18 | 0.2 | 1.8 | 0.12 | 0.01 | 0.0005 |

Vertical view of the leak paths considered in this study are shown in Figs. 2-4.

The pressure, which acts on the lower surface of the top shield, used for benchmark calculation is given by the following equation, considering the core bubble pressure evolution during the quasi-static stage of the CDA [2]:

| P(t)=P0V0V0+Q(t)e-tτ | (1) |
| --- | --- |

where τ is the time constant (0.8 s), Po is the starting pressure of the quasi-static pressure value, 0.21 (MPa). Vo (81 m3) is the starting volume of the core bubble corresponding to pressure, Po(0.21 MPa). Q(t) is the quantity of sodium (volume) released from the reactor assembly, although it is neglected in the calculations as it is small compared to V0. τ is obtained from the model of core bubble fuel vapor condensation [2]. Obtained pressure history is shown in Fig. 5, and used by each participant as a common inlet pressure.

Fig. 2.	Vertical view of the leak paths considered in this study (type 1 and 2).

Fig. 3.	Vertical view of the leak paths considered in this study (type 3, 4 and 5).

Fig. 4.	Vertical view of the leak paths considered in this study (type 6 and 7).

Fig. 5.	Pressure history used for the benchmark calculation.

  - CALCULATION METHOD

NCEPU(China)

ANSYS FLUENT was used for the calculation of the sodium ejection in NCEPU. FLUENT has a wide range of model systems to provide leading turbulence simulation capabilities which include several popular versions of k-epsilon and k-omega models, as well as Reynolds stress models for highly anisotropic flows. It also provides advanced scale-solving turbulence models, including large eddy simulation (LES), separated eddy simulation (DES), and adaptive eddy simulation (SAS). In this study, the standard k-e was established by NCEPU. The commercial software ICEM CFD was used to build the models needed for this study. Except for the two main leakage channels, the other channels have similar geometric characteristics. They have similar geometric features, with an "inverted L" shape. The geometric model of the fluid domain is established based on known parameters, and the model is meshed with ICEM CFD to calculate the leakage of liquid sodium using FLUENT.

The movement of liquid sodium in the RS-FTP gap channel under severe reactor accidents is at first explained. NCEPU attempted to create a 360° "inverted L" leaky channel model (Fig. 6). The pressure boundary conditions are compiled into a user-defined function (UDF), and the change in leakage at the outlet over time is calculated in FLUENT. Other leak paths are also modelled based on the above methods. Different “inverted L” leak paths are modelled and calculated separately according to the corresponding dimensions.

The flow field is a constant flow. The turbulence model selects the Standard k-e model. The wall uses an algorithm to select the Standard function. The outlet surface pressure is atmospheric pressure.

Fig. 6. A 360° "inverted L" leaky channel model

IBRAE RAN(Russia)

An universal integrated computer code, EUCLID/V2, is being developed at IBRAE RAN. The code is intended for the safety analysis of employed and designed fast reactors with liquid metal coolants (lead, lead-bismuth and sodium) at all operation regimes, including severe accidents. The first module integral EUCLID/V2 code used for this simulation is system thermal-hydraulic code HYDRA-IBRAE/LM. It allows performing calculation of non-stationary thermo-hydraulics applied to reactor loops and experimental facilities with liquid metal coolants, including a capability to describe the behavior of the water circuit and heat exchange equipment important for the safety of the NPP [3,4]. Computation of the thermal-hydraulic processes in HYDRA-IBRAE/LM is based on the non-equilibrium nonhomogeneous two- or three-fluid model.

The correlations for the calculations of friction pressure losses, heat exchange with wall and interphase interactions used in the thermohydraulic module were obtained mainly in FSUE "SSC RF – IPPE" on the basis of analysis of experimental data. Local pressure loss Δp are determined as follows:

| Δp=ζρu22 | (2) |
| --- | --- |

where ζ is coefficient of local resistance, u is average coolant velocity, and ρ is coolant density. Coefficient of local resistance is determined depending on the change of the flow area, whether the channel is the bend or the T-branch.

Nodalization scheme for penetrations consists of vertical and horizontal annular channel, as shown in Fig. 7.

P0tτV0Q(t)t (calculated parameter) Outlet pressure assumed to be atmospheric pressure. Sodium temperature is 900 K. For initial conditions inside leak paths next situation was explored: initially leak path volumes are filled with sodium.

| - Simple leak path | - RS-LRP and LRP-SRP |
| --- | --- |

Fig. 7. Nodalization scheme for simple leak path, RS-LRP and LRP-SRP penetrations.

IGCAR(India)

In order to perform the calculations of the quantity of the sodium released into the containment, a general-purpose hydraulic network model was developed to determine the leak rate of sodium mass through various sections of the leak paths in the top shield. The equations that govern the leak rate are based on force balance between flow resistance, inertia of sodium mass in various sections of leak paths, gravitational force, and upward force acting due to the quasi-static core bubble pressure [5,6]. A network model, NETFLOW, is developed to simulate the sodium flow through gaps between the top shield components. The network model is useful for modelling arbitrary leak paths. A basic equation of force balance for a path is written as follows:

| m1dv1dt=A1p1-p2-ki1v1v1+ fg1 ( θ1) | (3) |
| --- | --- |

where m1 is the mass and v1 is the velocity of the sodium in a path, A1 is the area and ki1 is the loss coefficient of a path, p1-p2 is the pressure difference in a path, fg1 is the gravitational force of the sodium in a path.

All the leak paths are modelled, though the major leakage paths are RS-LRP and LRP-SRP which consist of two branches, as can be seen in Fig. 8. The flow resistance in the leak paths depends on type of the flow, geometrical features of the flow channels, flow area etc. For this calculation, the loss coefficients were adapted from the open literature [7].

| Pr=Poe-tτVoVo+Q(t) |  |
| --- | --- |

τPoVoPo(0.21 MPa)QQ(t)τ

Fig. 8. Flow network model of a typical sodium leak path in top shield. Nodes n1, n3 and n5 are boundary nodes.

JAEA(Japan)

JAEA utilized the PLUG code, which was developed to model the dynamic movement of shield plugs and connecting bolts that fix them, and to evaluate the amount of sodium ejected onto the top shield through the gaps between the plugs using the pressure difference above and below the shield plugs. In this project, the amount of sodium ejected onto the top shield is calculated without calculating the dynamic movement of the plugs, assuming that each of the leak path is opened with a certain gap width in advance as an initial condition. In PLUG code, the amount of sodium ejected to the space above top shield is calculated based on the modified Bernoulli's equation:

| P1+ρgH1+12ρV12=∑∆p+P0+ρgH0+12ρV02 | (4) |
| --- | --- |

where P is pressure (Pa), ρ is density (kg/m3), g is gravity acceleration (m/s2), H is height from reference level (m), V is velocity (m/s), 0 is subscript indicating position 0 (outlet), 1 is subscript indicating position 1 (inlet), ∑∆p is the sum of all the friction and singular loss (Pa).

Equation (4) is steady-state equation which doesn’t include the time derivative term. PLUG code calculates the amount of sodium ejected in each time step by solving equation (4) with the pressure difference between above and below the top shield assuming that the gaps between plugs are filled with liquid sodium and the flow there is in steady-state. Friction loss in the vertical flow path, horizontal flow path and singular loss of bend and inlet section is calculated using Darcy-Weisbach equation. Vertical flow path is modelled as a concentric ring, and horizontal flow part is modelled as a path with rectangular cross section, which width, height and depth are respectively perimeter of large concentric ring, height of concentric ring and difference of radii between large and small ring, as shown in Fig. 9. Cross sectional area of inlet side of bend and narrow side of inlet section is used for velocity calculation. Resistance coefficient of 1.0 is given for all bend and narrow inlet section (except the first entrance). All the paths listed in Table 1 are modelled in this study.

(a) vertical flow path                        (b) horizontal flow path

Fig. 9. Flow path model of PLUG code.

CALCULATION RESULTS AND DISCUSSION

    - Results with common pressure

The leaked sodium mass calculated by each participant is compared on Table 3 and Fig. 10. Overall, the calculation results of all the participants are similar. This indicates that the variation in modelling for this calculation is small, and that the accuracy of the analysis methods of each institution are almost the same. In the process of liquid sodium passing through the top shield, there are two main leak paths: RS-LRP and LRP-SRP. As shown in Table 3, total released sodium is about ~330 kg, and about 80 % of total sodium released comes from the RS-LRP and LRP-SRP leak paths.

Fig. 11 shows the sodium leakage rate calculated by each participant. The leakage rate of sodium peaked out at about 0.1 s with the peak value being 400-500 kg/s in NCEPU, IBRAE and IGCAR, and then decreased to zero. The result of JAEA calculation is different from those of others especially flow rate change at the beginning. This is due to the fact that the time derivative is considered in the basic equation adopted in NCEPU, IBRAE and IGCAR although that it is not considered in JAEA. However, the amount sodium ejected in JAEA calculation is 335 kg, and this is not so different from those of IBRAE and IGCAR. This result can be explained that at the beginning of the leak, mass flow rate is greater in JAEA calculation, whereas at the end of the leak, mass flow rate decreases rapidly in JAEA calculation due to no inertia effect. As a result, the total leaked mass become comparable with IBRAE and IGCAR.

TABLE 3.	TOTAL LEAKED MASS FROM EACH LEAK PATHS

| Leak Paths | NCEPU** | IBRAE RAN | IGCAR | JAEA |
| --- | --- | --- | --- | --- |
| RS-LRP | 149.8 | 150.6 | 150.5 | 141.1 |
| LRP-SRP | 93.3 | 108.0 | 103.7 | 95.9 |
| RS-IHX/PSP (4/2)* | 33.8 | 41.0 | 36.2 | 44.0 |
| SRP-CP | 14.3 | 15.6 | 14.5 | 19.7 |
| SRP-OSP | -- | 11.5 | 8.57 | 12.1 |
| RS-DHX (4)* | 6.5 | 7.6 | 6.84 | 8.8 |
| Others | 10.0 | 11.0 | 9.29 | 13.4 |
| Total: | 307.7 | 345.1 | 329.6 | 334.9 |

* Value in the bracket corresponds to the number of the component.

** Inlet pressure of NCEPU is +10 kPa greater than the reference pressure.

* Inlet pressure of NCEPU is +10 kPa greater than the reference pressure.

Fig. 10. Leaked sodium mass calculated by each participant.

* Inlet pressure of NCEPU is +10 kPa greater than the reference pressure.

Fig. 11. Sodium ejection rate at the leak path RS-LRP calculated by each participant.

Sensitivity study

The result of NCEPU calculation listed in Table 3 was obtained when they use inlet pressure +10 KPa of the reference one. With the reference inlet pressure, NCEPU obtained the leaked sodium mass of 267.6 kg (87 % of the value listed in Table 3). The reason of less sodium ejection in NCEPU calculation is probably due to the difference of the calculation model. NCEPU uses the multi-dimensional flow model whereas the other participants use one-dimensional model.

In IBRAE, the sensitivity of grid size was investigated. They gave different grid size of 0,5*N, N and 2*N, where N is cell number for nominal case. The results show that there is no difference of the leaked sodium mass with the parameters given here, as shown in Fig. 12. The influence of input parameters on the calculation results was also investigated in IBRAE. In a series of calculations, following input parameters were varied: sodium temperature, inlet and outlet pressure and cross-section area. Changing ranges for the parameters are: 1) sodium temperature, ±50K, 2) inlet pressure, ±5%, 3) outlet pressure, 0-10 kPa, and 4) cross-section area, ±3%. Results of sensitivity study are presented in Fig. 12. The inlet and outlet pressure have the greatest influence on the calculation results. Injected sodium mass varies from 297.8 to 370.5 kg (86 % to 107 % of the reference case).

(a) sensitivity of grid size                      (b) influence of input parameters

Fig. 12. Results of the parametric analyses carried out in IBRAE.

A sensitivity study was performed in IGCAR to study effect of loss coefficients on the leaked sodium amounts. Two cases were considered viz., 1) the entry coefficients are neglected 2) the loss coefficient for bend is varied from 1.0 to 0.3. As shown in Fig. 13, when entry coefficients are neglected, the peak mass flow rates in leak path RS-LRP increase by ~25 Kg/sec, which leads to 10 Kg increase in leaked sodium from the reference case. When the bend coefficients are varied from 1.0 to 0.3, the peak mass flow rate increases by 120 Kg/sec. This leads to ~47 Kg increase in the leaked sodium from the reference case in leak path RS-LRP. This amounts to 409 kg of the total amount of leaked sodium (131 % of the reference case). These results indicate that the mass flow rates are sensitive to the loss coefficients; the accurate estimation of the loss coefficient is crucial.

Fig. 13. Sensitivity study of loss coefficient on sodium leak in IGCAR.

Pressure parameter case in JAEA

JAEA carried out a parameter case calculation with varying inlet pressure history. Inlet pressure history was calculated by SIMMER code [8], where molten fuel and steel ejection from the core region to the upper sodium plenum, and resultant FCI which gives pressure loading onto the top shield were modelled and calculated. The pressure history used in the calculation and the calculated sodium flow rate are plotted on Fig. 14. As shown in Fig. 14, there are several pressure peaks due to multiple but not so strong slug impact onto the lower surface of the top shield which are the result of multiple FCIs in the upper sodium plenum. This pressure history gives multiple peaks of the mass flow rate. The amount of sodium ejected from all the leak paths is 1840 kg in this pressure parameter case, whereas it is 335 kg in reference case. The reason of the sodium mass increase is not only peak pressure increase relative to the reference case from 0.2 MPa to 0.7 MPa but also duration increase of the pressure loading from 0.5 s to 1.5 s.

(a) Inlet pressure                    (b) Mass flow rate of the leaked sodium

Fig. 14.	Pressure parameter case in JAEA.

DISCUSSION

In this benchmark analysis, it is assumed that the leak path is filled with sodium as the initial condition in all the participants. This ignores the transients that sodium flows into the leak path. In reality, the sodium enters into the gaps between the plugs after the sodium slug impacts on the lower surface of the top shield, and only after the gap capacity being filled with the sodium, it outflows onto the top shield. The approximate capacity of the gaps between the plugs is shown in Table 4. In the estimation of the capacity, liquid sodium density is assumed to 820 kg/m3 (~550 °C), and only the volume of vertical and horizontal part of the leak paths is considered (volume of the bends is excluded). Since the leaked mass obtained by the calculation of the reference and parameter cases in NCEPU, IBRAE and IGCAR is less than this gap capacity, the sodium does not outflow onto the top shield if this gap capacity is taken into consideration. The amount of leaked mass is 75 kg in the pressure parameter case in JAEA when the gap capacity is taken into account.

TABLE 4.	CAPACITY OF THE LEAK PATH

| Leak Paths | Capacity (in kg of sodium) |
| --- | --- |
| RS-LRP | 908 |
| LRP-SRP | 460 |
| RS-IHX/PSP | 1214 (6*205) |
| SRP-CP | 213 |
| SRP-OSP | 34 |
| RS-DHX | 108 (4*27) |
| Others | 256 |
| Total: | 3223 |

In this benchmark analysis, each of the leak path being opened at a certain width in advance was assumed as the calculation condition, and the amount of sodium ejected onto the top shield was compared. In reality, ordinary plugs including roof slab are fixed with bolts, and rotating plugs are often fixed with freeze seals and then prevention measures for the missile are taken. Therefore, even if the pressure increases in the reactor vessel, the plugs will not move upward nor open the leak path onto the top shield unless the pressure exceeds the weight of the plug and the force of the bolt. In order to evaluate this effect, it is necessary to analyse the dynamic response of the plugs.

In this benchmark analysis, design clearances (as built) of the leak path were used. This clearance may vary with aging or sodium mist deposition onto the path wall. These effects probably result in narrowing the leak paths and are better to be considered.

CONCLUSIONS

Four institutions participating in this CRP conducted benchmark analyses of sodium ejection. In the analyses using a common pressure history (reference case), the results of the analysis of each institution were in good agreement. This indicates that the variation in modelling for this task is small, and that the accuracy of the analysis methods of each institution are almost the same. The amount of sodium ejected onto the top shield calculated in reference case is conservatively approximated to be 350 kg and will be utilized in WP-3 as input for primary system/containment system interface source term calculation and sodium combustion calculation.

According to the results of the parameter analyses performed here, the change of parameters regarding uncertainty, such as input pressure, outlet pressure, cross-sectional area, and loss coefficient bring about the change of leaked mass in the range of several tens of %.

It is assumed in this benchmark analysis that the leak paths have already opened and filled with sodium as the initial condition in all the institutions. This ignores the transients that sodium flows into the leak paths between the plugs. In reality, the sodium flows into the leak paths after the sodium slug impacts on the lower surface of the top shield, and only after the leak paths being filled with the sodium, it outflows onto the top shield. Considering the volume of the leak paths, sodium is not ejected onto the top shield if we use a common pressure history, and the ejection amount is about 75 kg even in the case of the JAEA pressure parameter case.

Ordinary plugs including roof slab are fixed with bolts, and rotating plugs are often fixed with freeze seals and then prevention measures for them being missile are taken. Therefore, even if the pressure increases in the reactor vessel, the plugs will not move upward nor open the leak paths onto the top shield unless the pressure exceeds the weight of the plugs and the force of the bolts. In order to evaluate this effect, it is necessary to analyse the dynamic response of the plugs.

Abbreviations

RS		Roof Slab

LRP		Large Rotating Plug

SRP		Small Rotating Plug

CP		Control Plug

IHX		Intermediate Heat Exchanger

PSP		Primary Sodium Pump

CPLD		Cold Pool Level Detector

DHX		Decay Heat Exchanger

FTP		Fuel Transfer Port

FTMBF		Fuel Transfer Machine Bottom Flange

DND		Delayed Neutron Detector

OSP		Oval Shield Plug of Transfer Arm

GT		Guide Tube

FFIM		Failed Fuel Identification Module

HPLD		Hot Pool Level Detector

CSRDM	Control and Safety Rod Drive Mechanisms

DSRDM	Diverse Safety Rod Drive Mechanisms

References

- [1]	ARUL, J. et al., Source term estimation for radioactivity release under severe accident scenarios in sodium cooled fast reactors, Fast Reactors and Related Fuel Cycles: Next Generation Nuclear Systems for Sustainable Development FR17 (Proc. Int. Conf., Yekaterinburg, 2017), IAEA, Vienna (2018), Paper CN245-335.

- [2]	K. Velusamy, P. Chellapandi, K. Satpathy, N. Verma, G.R. Raviprasan, M. Rajendrakumar, S.C. Chetal, A fundamental approach to specify thermal and pressure loadings on containment buildings of sodium cooled fast reactors during a core disruptive accident, Ann. Nucl. Energy. 38 (2011) 2475–2487.

- [3]	Alipchenkov, V.M., Zeigarnik, Y.A., Mosunova, N.A., Strizhov, V.F., Usov, E.V., Anfimov, A.M., Gorbunov, V.S., Osipov, S.L., Afremov, D.A., Kudryavtsev, A.V., Fundamentals, current state of the development of, and prospects for further improvement of the new-generation thermal-hydraulic computational HYDRA-IBRAE/LM code for simulation of fast reactor systems, Thermal Engineering, 63(2) (2016) 130–139.

- [4]	Mosunova N.A., The EUCLID/V1 Integrated Code for Safety Assessment of Liquid Metal Cooled Fast Reactors. Part 1: Basic Models, Thermal Engineering 65(5), (2018) 304–316.

- [5]	D.D. Stepnewski, G.L. Fox, R.D. Peak, K.R. Merckx, Mechanical Consequences of Hypothetical Core Disruptive Accidents, Hanford Engineering Development Lab., Richland, Wash. (1971), https://doi.org/10.2172/4753798.

- [6]	N.E. Todreas, M.S. Kazimi, Nuclear systems. 1: Thermal hydraulic fundamentals, First, Hemisphere Publication Corporation, New York, 1993.

- [7]	P. Chellapandi, K. Velusamy, S.C. Chetal, S.B. Bhoje, H. Lal, V.S. Sethi, Analysis for Mechanical Consequences of a Core Disruptive Accident in Prototype Fast Breeder Reactor, INIS-CZ-0039, SMIRT 17, International conference on structural mechanics in reactor technology, Prague (Czech Republic), 17-22, Aug 2003.

- [8]	INTERNATIONAL ATOMIC ENERGY AGENCY, Modelling and Simulation of Source Term for Sodium Cooled Fast Reactor under Hypothetical Severe Accident, Final Report of the IAEA Coordinated Research Project on “Radioactive Release from the Prototype Sodium Cooled Fast Reactor under Severe Accident Conditions”, IAEA, Vienna (to be published).

___________________________________________________________________________

___________________________________________________________________________