## Slide 2: Economic Analysis of Thermal Energy Storage Integration in Small Modular Reactors Balance of Plant
F. Tassone, G. Locatelli, S. Lorenzi, M. E. Ricotti

## Slide 3
Agenda
Introduction
  Storage and nuclear technologies
  Power plant configurations
  Hypotheses and notes
Methodology and results
  Estimation of costs
  Estimation of revenues
  Discounted cash flow
Comments and conclusions
2

## Slide 4
Introduction
3
In 2022 alone, share of renewable energy sources increased by 340 GWe.
The ability to modulate electricity output is becoming increasingly valuable, especially for base load power plants, like nuclear (NPPs).
Load-following with NPPs is possible but usually avoided:
  increased thermo-mechanical stresses among reactor components;
  reduced power output (loss in revenues) with constant operational costs.
Energy storage could enhance load-following capabilities of NPPs.
Constant power output:
  Price arbitrage;
  Operational easiness.

## Slide 5
Introduction
4
Energy storage technologies:
Mechanical - e.g., pumped hydro, compressed air;
Chemical - e.g., batteries;
Electrical - e.g., capacitors;
Thermal - e.g., molten salt.
  Molten salt thermal energy storage (MSTES).
  Solar salt (40% KNO3, 60% NaNO3).
  Working temperatures: 290°C for cold tank, 400°C for hot tank.
Nuclear technologies:
Gen IV technologies would be more suitable for such coupling given the higher temperatures reached with respect to typical Gen II, III/III+ NPPs;
One of the most advanced in research is the lead-cooled fast reactor (LFR);
ALFRED, European demonstrator for lead technology, given its advanced design status and temperature compatibility (450°C in the steam loop), is the reactor selected for this study.

## Slide 6
ALFRED-MSTES plant configurations
5
Notation:
U1, U2, U3 - unloading scheme and turbine size;
L1, L2 - loading scheme;
S1, S2, S3 - storage size.
M. Celador Lera et al. Main components definition: definition and sizing of the main components, including sensitivity analysis of both BOP configurations. ANSELMUS, D5.2, 2023.
ALFRED
HPT
LPT
Cold tank
Hot tank
Condenser
ALFRED
HPT
LPT
Cold tank
Hot tank
Condenser
Simplified loading scheme
Simplified unloading scheme

## Slide 7
ALFRED-MSTES plant configurations
6
3 countries: Germany, Italy, and Romania.
Total scenarios: 18 configurations × 3 countries = 54 possibilities.
Examples: U2-L1-S2 in Italy, U3-L2-S1 in Romania, etc.
Reactor | LFR | ALFRED: 300 MWt, 118 MWe.
Loading and Unloading Schemes | U1-L1 | Plant net power when loading and unloading: 80.6 and 136.0 MWe. Unloading/loading time ratio: 1.44.
 | U1-L2 | Plant net power when loading and unloading: 41.5 and 136.0 MWe. Unloading/loading time ratio: 2.87.
 | U2-L1 | Plant net power when loading and unloading: 73.6 and 153.6 MWe. Unloading/loading time ratio: 0.72.
 | U2-L2 | Plant net power when loading and unloading: 35.0 and 153.6 MWe. Unloading/loading time ratio: 1.43.
 | U3-L1 | Plant net power when loading and unloading: 68.3 and 187.1 MWe. Unloading/loading time ratio: 0.36.
 | U3-L2 | Plant net power when loading and unloading: 30.1 and 187.1 MWe. Unloading/loading time ratio: 0.72.
Tanks | S1 | Total salt: 12000 ton. Diameter: 24.2 m. Height: 14 m.
 | S2 | Total salt: 15000 ton. Diameter: 27.1 m. Height: 14 m.
 | S3 | Total salt: 20000 ton. Diameter: 31.3 m. Height: 14 m.

## Slide 8
ALFRED-MSTES plant configurations
6
Reactor | LFR | ALFRED: 300 MWt, 118 MWe.
Loading and Unloading Schemes | U1-L1 | Plant net power when loading and unloading: 80.6 and 136.0 MWe. Unloading/loading time ratio: 1.44.
 | U1-L2 | Plant net power when loading and unloading: 41.5 and 136.0 MWe. Unloading/loading time ratio: 2.87.
 | U2-L1 | Plant net power when loading and unloading: 73.6 and 153.6 MWe. Unloading/loading time ratio: 0.72.
 | U2-L2 | Plant net power when loading and unloading: 35.0 and 153.6 MWe. Unloading/loading time ratio: 1.43.
 | U3-L1 | Plant net power when loading and unloading: 68.3 and 187.1 MWe. Unloading/loading time ratio: 0.36.
 | U3-L2 | Plant net power when loading and unloading: 30.1 and 187.1 MWe. Unloading/loading time ratio: 0.72.
Tanks | S1 | Total salt: 12000 ton. Diameter: 24.2 m. Height: 14 m.
 | S2 | Total salt: 15000 ton. Diameter: 27.1 m. Height: 14 m.
 | S3 | Total salt: 20000 ton. Diameter: 31.3 m. Height: 14 m.
3 countries: Germany, Italy, and Romania.
Total scenarios: 18 configurations × 3 countries = 54 possibilities.
Examples: U2-L1-S2 in Italy, U3-L2-S1 in Romania, etc.

## Slide 9
ALFRED-MSTES plant configurations
6
Reactor | LFR | ALFRED: 300 MWt, 118 MWe.
Loading and Unloading Schemes | U1-L1 | Plant net power when loading and unloading: 80.6 and 136.0 MWe. Unloading/loading time ratio: 1.44.
 | U1-L2 | Plant net power when loading and unloading: 41.5 and 136.0 MWe. Unloading/loading time ratio: 2.87.
 | U2-L1 | Plant net power when loading and unloading: 73.6 and 153.6 MWe. Unloading/loading time ratio: 0.72.
 | U2-L2 | Plant net power when loading and unloading: 35.0 and 153.6 MWe. Unloading/loading time ratio: 1.43.
 | U3-L1 | Plant net power when loading and unloading: 68.3 and 187.1 MWe. Unloading/loading time ratio: 0.36.
 | U3-L2 | Plant net power when loading and unloading: 30.1 and 187.1 MWe. Unloading/loading time ratio: 0.72.
Tanks | S1 | Total salt: 12000 ton. Diameter: 24.2 m. Height: 14 m.
 | S2 | Total salt: 15000 ton. Diameter: 27.1 m. Height: 14 m.
 | S3 | Total salt: 20000 ton. Diameter: 31.3 m. Height: 14 m.
3 countries: Germany, Italy, and Romania.
Total scenarios: 18 configurations × 3 countries = 54 possibilities.
Examples: U2-L1-S2 in Italy, U3-L2-S1 in Romania, etc.

## Slide 10
Hyphotheses and notes
7
‘Differential’ analysis. We are not considering cost and revenues common to all scenarios (including e.g., capital investment for the nuclear reactor). We are estimating the increase in total capital investment (TCI), operational costs (O&M) and revenues generated by the coupling with the MSTES:
  MSTES - capital investment and O&M costs;
  ALFRED - increase in capital cost, increase in O&M assumed zero for the reactor.
The plants (ALFRED + MSTES) are considered First-Of-A-Kinds (FOAKs).
Molten salt is loaded during hours with lowest electricity price, it is unloaded when price is high (price arbitrage), also for not consecutive hours. Salts cannot be loaded and unloaded simoultaneously.
All costs and prices are expressed in 2022 USD ($).

## Slide 11
[M$] | MSTES |  | NPP |  | MSTES |  | NPP
 | TCI | Annual O&M costs | Increase in NPP costs |  | TCI | Annual O&M costs | Increase in NPP costs
U1-L1-S1 | 76 | 3 | 9 | U2-L2-S1 | 87 | 3 | 17
U1-L1-S2 | 85 | 3 | 9 | U2-L2-S2 | 97 | 4 | 17
U1-L1-S3 | 106 | 4 | 9 | U2-L2-S3 | 109 | 4 | 17
U1-L2-S1 | 84 | 3 | 9 | U3-L1-S1 | 94 | 4 | 32
U1-L2-S2 | 92 | 4 | 9 | U3-L1-S2 | 101 | 4 | 32
U1-L2-S3 | 114 | 5 | 9 | U3-L1-S3 | 115 | 5 | 32
U2-L1-S1 | 79 | 3 | 17 | U3-L2-S1 | 101 | 4 | 32
U2-L1-S2 | 89 | 4 | 17 | U3-L2-S2 | 109 | 4 | 32
U2-L1-S3 | 102 | 4 | 17 | U3-L2-S3 | 122 | 5 | 32
Cost estimation
8
D. E. Holcomb et al., Advanced high temperature reactor systems and economic analysis. ORNL/TM-2011/364. 2011.
M. Shamoushaki et al., Development of cost correlations for the economic assessment of power plant equipment. Energies 14 (2021), 2665.
S. Thaker et al., Techno-economic evaluation of solar-based thermal energy storage systems. Energy Conversion and Management 153 (2017), 423-434.
B. Kelly and D. Kearney. Thermal storage commercial plant design study for a 2-tank indirect molten salt system. NREL/SR-550-40166. 2006.
R. Smith. Chemical process design and integration. John Wiley and Sons, Ltd. 2005.
F. Ganda et al., Report on the update of fuel cycle cost algorithms. NTRD-FCO-2018-000439. 2018.

## Slide 12
Cost estimation
8
D. E. Holcomb et al., Advanced high temperature reactor systems and economic analysis. ORNL/TM-2011/364. 2011.
M. Shamoushaki et al., Development of cost correlations for the economic assessment of power plant equipment. Energies 14 (2021), 2665.
S. Thaker et al., Techno-economic evaluation of solar-based thermal energy storage systems. Energy Conversion and Management 153 (2017), 423-434.
B. Kelly and D. Kearney. Thermal storage commercial plant design study for a 2-tank indirect molten salt system. NREL/SR-550-40166. 2006.
R. Smith. Chemical process design and integration. John Wiley and Sons, Ltd. 2005.
F. Ganda et al., Report on the update of fuel cycle cost algorithms. NTRD-FCO-2018-000439. 2018.
[M$] | MSTES |  | NPP |  | MSTES |  | NPP
 | TCI | Annual O&M costs | Increase in NPP costs |  | TCI | Annual O&M costs | Increase in NPP costs
U1-L1-S1 | 76 | 3 | 9 | U2-L2-S1 | 87 | 3 | 17
U1-L1-S2 | 85 | 3 | 9 | U2-L2-S2 | 97 | 4 | 17
U1-L1-S3 | 106 | 4 | 9 | U2-L2-S3 | 109 | 4 | 17
U1-L2-S1 | 84 | 3 | 9 | U3-L1-S1 | 94 | 4 | 32
U1-L2-S2 | 92 | 4 | 9 | U3-L1-S2 | 101 | 4 | 32
U1-L2-S3 | 114 | 5 | 9 | U3-L1-S3 | 115 | 5 | 32
U2-L1-S1 | 79 | 3 | 17 | U3-L2-S1 | 101 | 4 | 32
U2-L1-S2 | 89 | 4 | 17 | U3-L2-S2 | 109 | 4 | 32
U2-L1-S3 | 102 | 4 | 17 | U3-L2-S3 | 122 | 5 | 32
Less expensive configuration
85 M$ and 3 M$ increase in annual O&M
Most expensive configuration
154 M$ and 5 M$ increase in annual O&M

## Slide 13
Revenues estimation
9
Revenues come solely from the selling of electricity.
For simplicity:
  Daily analysis considering the average electricity price in a day for 2023;
  Each day, the molten salt loaded is equal to the amount unloaded;
  Estimation of the maximum daily increase in revenues.
2023 electricity prices of Germany, Italy, and Romania.
https://transparency.entsoe.eu/

## Slide 14
Chart: Hour of the day
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 day | 120.4183 | 114.5901 | 110.427 | 108.0018 | 108.2592 | 113.6206 | 126.8495 | 140.5272 | 148.0951 | 138.2392 | 124.7553 | 117.3603 | 109.1288 | 105.37 | 109.506 | 116.5855 | 127.061 | 138.0859 | 151.1149 | 166.9035 | 159.6074 | 145.0471 | 131.4805 | 122.9462
2 days - Summer | 113.4428 | 108.375 | 105.022 | 103.0262 | 103.074 | 106.5726 | 115.2182 | 127.4671 | 130.8108 | 120.4363 | 109.1382 | 102.3859 | 94.1783 | 90.1189 | 92.4746 | 97.0888 | 104.9236 | 113.8734 | 128.0015 | 152.6994 | 157.9491 | 143.4968 | 124.7279 | 115.5498
2 days - Winter | 127.5094 | 120.9082 | 115.9215 | 113.0599 | 113.5304 | 120.7854 | 138.6735 | 153.8038 | 165.6658 | 156.3372 | 140.6312 | 132.5829 | 124.3271 | 120.8738 | 126.8196 | 136.4054 | 149.5653 | 162.6997 | 174.6115 | 181.343 | 161.2932 | 146.6231 | 138.345 | 129.0321
Weekdays | 119.7815 | 112.8187 | 108.6773 | 106.5803 | 107.2736 | 114.3382 | 130.6212 | 148.2503 | 159.2472 | 147.2064 | 131.9018 | 124.9613 | 115.5334 | 114.2981 | 120.0072 | 126.2784 | 134.9883 | 144.0256 | 155.7189 | 171.0518 | 161.3989 | 145.8198 | 131.8858 | 122.6746
Weekend | 121.9951 | 118.9763 | 114.7596 | 111.5216 | 110.6996 | 111.8435 | 117.5099 | 121.4035 | 120.4803 | 116.0348 | 107.0591 | 98.5388 | 93.27 | 83.2623 | 83.5029 | 92.5841 | 107.4314 | 123.3781 | 139.7144 | 156.6315 | 155.1715 | 143.1339 | 130.4768 | 123.6316
Annual average | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492
Revenues estimation
9
Revenues come solely from the selling of electricity.
For simplicity:
  Daily analysis considering the average electricity price in a day for 2023;
  Each day, the molten salt loaded is equal to the amount unloaded;
  Estimation of the maximum daily increase in revenues.
2023 electricity prices of Germany, Italy, and Romania.
Chart: Hour of the day
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 day | 120.4183 | 114.5901 | 110.427 | 108.0018 | 108.2592 | 113.6206 | 126.8495 | 140.5272 | 148.0951 | 138.2392 | 124.7553 | 117.3603 | 109.1288 | 105.37 | 109.506 | 116.5855 | 127.061 | 138.0859 | 151.1149 | 166.9035 | 159.6074 | 145.0471 | 131.4805 | 122.9462
Annual average | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492
Example: Italy’s electricity price in 2023
https://transparency.entsoe.eu/

## Slide 15
Chart: Hour of the day
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 day | 120.4183 | 114.5901 | 110.427 | 108.0018 | 108.2592 | 113.6206 | 126.8495 | 140.5272 | 148.0951 | 138.2392 | 124.7553 | 117.3603 | 109.1288 | 105.37 | 109.506 | 116.5855 | 127.061 | 138.0859 | 151.1149 | 166.9035 | 159.6074 | 145.0471 | 131.4805 | 122.9462
2 days - Summer | 113.4428 | 108.375 | 105.022 | 103.0262 | 103.074 | 106.5726 | 115.2182 | 127.4671 | 130.8108 | 120.4363 | 109.1382 | 102.3859 | 94.1783 | 90.1189 | 92.4746 | 97.0888 | 104.9236 | 113.8734 | 128.0015 | 152.6994 | 157.9491 | 143.4968 | 124.7279 | 115.5498
2 days - Winter | 127.5094 | 120.9082 | 115.9215 | 113.0599 | 113.5304 | 120.7854 | 138.6735 | 153.8038 | 165.6658 | 156.3372 | 140.6312 | 132.5829 | 124.3271 | 120.8738 | 126.8196 | 136.4054 | 149.5653 | 162.6997 | 174.6115 | 181.343 | 161.2932 | 146.6231 | 138.345 | 129.0321
Weekdays | 119.7815 | 112.8187 | 108.6773 | 106.5803 | 107.2736 | 114.3382 | 130.6212 | 148.2503 | 159.2472 | 147.2064 | 131.9018 | 124.9613 | 115.5334 | 114.2981 | 120.0072 | 126.2784 | 134.9883 | 144.0256 | 155.7189 | 171.0518 | 161.3989 | 145.8198 | 131.8858 | 122.6746
Weekend | 121.9951 | 118.9763 | 114.7596 | 111.5216 | 110.6996 | 111.8435 | 117.5099 | 121.4035 | 120.4803 | 116.0348 | 107.0591 | 98.5388 | 93.27 | 83.2623 | 83.5029 | 92.5841 | 107.4314 | 123.3781 | 139.7144 | 156.6315 | 155.1715 | 143.1339 | 130.4768 | 123.6316
Annual average | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492
Revenues estimation
9
Revenues come solely from the selling of electricity.
For simplicity:
  Daily analysis considering the average electricity price in a day for 2023;
  Each day, the molten salt loaded is equal to the amount unloaded;
  Estimation of the maximum daily increase in revenues.
2023 electricity prices of Germany, Italy, and Romania.
Note:
the increase in revenues is proportional to the area between the curve and its average value.
Chart: Hour of the day
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 day | 120.4183 | 114.5901 | 110.427 | 108.0018 | 108.2592 | 113.6206 | 126.8495 | 140.5272 | 148.0951 | 138.2392 | 124.7553 | 117.3603 | 109.1288 | 105.37 | 109.506 | 116.5855 | 127.061 | 138.0859 | 151.1149 | 166.9035 | 159.6074 | 145.0471 | 131.4805 | 122.9462
Annual average | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492 | 127.2492
Example: Italy’s electricity price in 2023
Loading hours
Unloading hours
https://transparency.entsoe.eu/

## Slide 16
Revenues estimation
10
Maximum increase in daily revenues

## Slide 17
Revenues estimation
10
Power while loading and nominal power
Power while unloading and nominal power
Maximum increase in daily revenues

## Slide 18
Revenues estimation
10
Power while loading and nominal power
Loading hours (integer)
Power while unloading and nominal power
Unloading hours (integer)
Maximum increase in daily revenues

## Slide 19
Revenues estimation
10
Electricity price: hour value and average
Power while loading and nominal power
Loading hours (integer)
Power while unloading and nominal power
Unloading hours (integer)
Maximum increase in daily revenues

## Slide 20
Revenues estimation
10
Correcting factor for last unloading hour
example:
loading time - 2 hours
unloading time - 3.4 hours
L = 2
U = 4
k1 = k2 = k3 = 1
k4 = 0.4
Electricity price: hour value and average
Power while loading and nominal power
Loading hours (integer)
Power while unloading and nominal power
Unloading hours (integer)
Maximum increase in daily revenues

## Slide 21
Revenues estimation
11
Total of 54 configurations.
A configuration is discarded when:
  maximum increase in revenues lower than daily increase in O&M;
  revenues equal to the ones of the smaller configuration (same U and L, but smaller S).
30 configurations are discarded.
24 remaining configurations:
  10 for Romania;
  8 for Italy;
  6 for Germany.
Differences are caused by the electricity price profiles.
Chart: Loading hours [h]
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
 | 10551
 | 13922
 | 17245
 | 18232
 | 11737
 | 15667
 | 18641
 | 27322
 | 10107
 | 13261
 | 19967
 | 18360
→ Germany
→ Italy
→ Romania
 | S1 | S2 | S3
U1L1 |  | - | -
U2L1 |  |  | -
U3L1 | - |  | 
U1L2 | - |  | -
U2L2 |  |  | -
U3L2 | - |  | 

## Slide 22
Discounted cash flow
12
Assumptions to compute Net Present Value (NPV):
MSTES lifetime of 30 years, with construction and decommissioning;
5% interest rate;
MSTES construction period of 2 years (year 1 and 2);
1 year decommissioning (year 30);
Load factor of 90%.

## Slide 23
Discounted cash flow
12
Assumptions to compute Net Present Value (NPV):
MSTES lifetime of 30 years, with construction and decommissioning;
5% interest rate;
MSTES construction period of 2 years (year 1 and 2);
1 year decommissioning (year 30);
Load factor of 90%.
NPV [M$] | Italy |  |  | Germany |  |  | Romania |  | 
 | S1 | S2 | S3 | S1 | S2 | S3 | S1 | S2 | S3
U1-L1 |  |  |  |  |  |  | -82 |  | 
U2-L1 | -92 | -92 |  | -83 | -83 |  | -80 | -65 | 
U3-L1 |  | -110 | -127 |  | -97 |  |  | -105 | -91
U1-L2 |  |  |  |  |  |  |  | -105 | 
U2-L2 | -99 | -96 |  |  | -89 |  | -108 | -70 | 
U3-L2 |  | -116 | -97 |  | -97 | -80 |  | -112 | -47

## Slide 24
Discounted cash flow
12
U3-L2-S3 is the prefereable choice for Germany and Romania.
For Italy, it has a worse NPV than others, however, its NPV can increase more easily.
We can state U3-L2-S3 is the preferable choice overall.
NPV [M$] | Italy |  |  | Germany |  |  | Romania |  | 
 | S1 | S2 | S3 | S1 | S2 | S3 | S1 | S2 | S3
U1-L1 |  |  |  |  |  |  | -82 |  | 
U2-L1 | -92 | -92 |  | -83 | -83 |  | -80 | -65 | 
U3-L1 |  | -110 | -127 |  | -97 |  |  | -105 | -91
U1-L2 |  |  |  |  |  |  |  | -105 | 
U2-L2 | -99 | -96 |  |  | -89 |  | -108 | -70 | 
U3-L2 |  | -116 | -97 |  | -97 | -80 |  | -112 | -47
Assumptions to compute Net Present Value (NPV):
MSTES lifetime of 30 years, with construction and decommissioning;
5% interest rate;
MSTES construction period of 2 years (year 1 and 2);
1 year decommissioning (year 30);
Load factor of 90%.

## Slide 25
Discounted cash flow
12
U3-L2-S3 is the prefereable choice for Germany and Romania.
For Italy, it has a worse NPV than others, however, its NPV can increase more easily.
We can state U3-L2-S3 is the preferable choice overall.
NPV [M$] | Italy |  |  | Germany |  |  | Romania |  | 
 | S1 | S2 | S3 | S1 | S2 | S3 | S1 | S2 | S3
U1-L1 |  |  |  |  |  |  | -82 |  | 
U2-L1 | -92 | -92 |  | -83 | -83 |  | -80 | -65 | 
U3-L1 |  | -110 | -127 |  | -97 |  |  | -105 | -91
U1-L2 |  |  |  |  |  |  |  | -105 | 
U2-L2 | -99 | -96 |  |  | -89 |  | -108 | -70 | 
U3-L2 |  | -116 | -97 |  | -97 | -80 |  | -112 | -47
Assumptions to compute Net Present Value (NPV):
MSTES lifetime of 30 years, with construction and decommissioning;
5% interest rate;
MSTES construction period of 2 years (year 1 and 2);
1 year decommissioning (year 30);
Load factor of 90%.

## Slide 26
Comments
13
All NPVs are negative, however:
the largest the configurations are preferable, U3-L2-S3 has the highest NPV;
we are considering the plant as a FOAK;
1-day approximation: peaks and valleys are smoother and broader, missing highest values.
we are considering only day-ahead market.
Moreover:
the maximum increase in revenues is proportional to the area between price curve and its average;
is that area proportional to the variation of daily electricity price (max - min)?

## Slide 27
Comments
13
Chart: Area above or below the average daily price [$]
All NPVs are negative, however:
the largest the configurations are preferable, U3-L2-S3 has the highest NPV;
we are considering the plant as a FOAK;
1-day approximation: peaks and valleys are smoother and broader, missing highest values.
we are considering only day-ahead market.
Moreover:
the maximum increase in revenues is proportional to the area between price curve and its average;
is that area proportional to the variation of daily electricity price (max - min)?

## Slide 28
Comments
13
Chart: Area above or below the average daily price [$]
What is the minimum variation in daily electricity price for which the configurations reach NPV = 0?
All NPVs are negative, however:
the largest the configurations are preferable, U3-L2-S3 has the highest NPV;
we are considering the plant as a FOAK;
1-day approximation: peaks and valleys are smoother and broader, missing highest values.
we are considering only day-ahead market.
Moreover:
the maximum increase in revenues is proportional to the area between price curve and its average;
is that area proportional to the variation of daily electricity price (max - min)?

## Slide 29
Comments
14
Chart: Increase in TCI [M$]
| 96.335101 | 106.356401 | 132.800716 | 146.582394 | 104.014454 | 114.035753 | 140.480068 | 154.261748
Italy | 184.6005 | 153.8338 | 147.6804 | 159.9871 | 178.4472 | 147.6804 | 147.6804 | 110.7603
Germany | 164.8269 | 145.0477 | 138.4546 | 145.0477 | 131.8615 | 105.4892
Romania | 239.0925 | 204.9364 | 153.7023 | 196.3974 | 153.7023 | 273.2485 | 213.4754 | 153.7023 | 196.3974 | 111.0072
Such daily variations would be increasingly common with an increasing share of renewables
U3-L2-S3 requires a daily electricity price variation of around 100 $/MWh to be profitable

## Slide 30
Chart: Increase in TCI [M$]
| 96.335101 | 106.356401 | 132.800716 | 146.582394 | 104.014454 | 114.035753 | 140.480068 | 154.261748
Italy | 184.6005 | 153.8338 | 147.6804 | 159.9871 | 178.4472 | 147.6804 | 147.6804 | 110.7603
Germany | 164.8269 | 145.0477 | 138.4546 | 145.0477 | 131.8615 | 105.4892
Romania | 239.0925 | 204.9364 | 153.7023 | 196.3974 | 153.7023 | 273.2485 | 213.4754 | 153.7023 | 196.3974 | 111.0072
Comments
14
Configuration U3-L2-S3 |  | 23rd January | 8th April | 10th August | 17th October
Germany | [k$/day] | 57 | 22 | 54 | 38
 | Daily variation | 124 | 46 | 167 | 94
Italy | [k$/day] | 44 | 32 | 20 | 25
 | Daily variation | 105 | 119 | 61 | 62
Romania | [k$/day] | 105 | 26 | 26 | 80
 | Daily variation | 235 | 70 | 94 | 200
Example days from 2023
U3-L2-S3 requires a daily electricity price variation of around 100 $/MWh to be profitable
Such daily variations would be increasingly common with an increasing share of renewables

## Slide 31
Conclusion
15
We performed an economic analysis of MSTES coupled with ALFRED, considering 18 configurations and 3 countries, for a total of 54 possibilities.
We evaluated the increase in capital cost due to MSTES at around 80-160 M$, depending on the configuration.
We performed an average-day analysis for the estimation of the increase in daily revenues. The results are around 10-40 k$/day, depending on the configuration.
The most promising configuration is U3-L2-S3, requiring a daily electricity price variation of 100 $/MWh to be profitable. Such variations would be more and more common with an increasing share of renewables.

## Slide 32: Economic Analysis of Thermal Energy Storage Integration in Small Modular Reactors Balance of Plant
F. Tassone, G. Locatelli, S. Lorenzi, M. E. Ricotti
federico.tassone@polimi.it - giorgio.locatelli@polimi.it - stefano.lorenzi@polimi.it - marco.ricotti@polimi.it
Thank you for your attention!